## Instructions
NCMA Fire Resistance Calculator
This spreadsheet provides section properties for CMU walls that are either vertically or horizontally grouted.
1. Orange cells are for user input
2. Grey cells with orange text are interim calculations with pertinent information.
3. Units must conform to a 2 faceshell configuration
4. Depending on user input, cells may appear or vanish based on what is needed. Leave no cells blank.
5. For a more detailed instruction, double-click the link below to be directed to a PDF (will open in Adobe Acrobat)
6. If you feel the need or desire to edit or alter the calculations in this sheet, the protection password is as follows:
bloxrox

## Fire Resistance
Date
Project Name
Project Number
Unit Description
Fire Rating Based on Single Wythe CMU Wall
***This section is meant for producers only! Designers should not use this section of the estimator to create their own mixes. Local producers should be consulted if the mix is needed to be determined.
Step 1: Enter Equivalent Thickness | [5 empty] | Refer to the SAAP Calculator for an estimated equivalent thickness based on provided dimensions.The subsequent calculations will not account for any tapering of the block.For more accurate calculations, enter the equivalent thickness given from an ASTM C140 Report.
Enter the Equivalent Thickness |  |  |  | 8
Step 2: Fill out the aggregate composition of the unit
% Volume Breakdown
Calcareous or Siliceous Gravel |  |  |  | 35
Limestone, Cinders or Unexpanded Slag |  |  |  | 25
Expanded clay, shale, or slate |  |  |  | 15
Expanded slag or pumice |  |  |  | 25
100%
Fire Rating Based on Multi Wythe CMU Wall
***This section is meant for designers if they wish to determine how to effect the fire rating with external components for a CMU wall.
Step 1: Enter Wythe Details
How many total wythes are present including the CMU wall? |  |  |  | 2
Select the desired layout of the mutli-wythe configuration |  |  |  | Clay / CMU
Do you wish to enter a fire rating or enter equivalent thickness for clay (brick, tile, or shale) or CMU wythe(s)? |  |  |  | Equivalent Thickness
Step 2a: Enter Equivalent Thickness of Wythe(s)
Enter the equivalent thickness of clay wythe #1 |  |  |  | 3 | in.
Step 2b: Enter Type of Clay Wythe(s)
What is clay wythe #1 material type? |  |  |  | >=75% Solid
0%
0%
Fire Rating Based on Finish Materials
***This section is meant for designers if they wish to determine how to effect the fire rating with external components for a CMU wall.
Step 1: Enter Assembly Description
**The option of a clay veneer and finish is a not a calculatable option due to multi-wythe walls typically obtaining a fire rating > 4 hrs.
What type of assembly is to be analyzed? |  |  |  | CMU Single Wythe with a finish on both sides
Step 2: Enter Non-Fire Side Finish Detail(s)
Non-Fire-Exposed Side
What type of finish is applied on one side (Finish #1) of the wythe? |  |  |  | Portland Cement Sand Plaster | 1
What is the aggregate type in concrete masonry |  |  |  | Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag
Yes
What type of finish is applied on the other side (Finish #2) of the wythe? |  |  |  | Gypsum Sand Plaster | 1.25
What is the aggregate type in concrete masonry |  |  |  | Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag
|  |  |  | 1/2 in. | 0.5
What is the Finish #1 thickness? |  |  |  | 3/8 in. | in.
What is the finish #2 thickness? |  |  |  | 1/2 in. | 0.5
Step 3: Enter Fire Side Finish Detail(s)
Fire-Exposed Side
Fire Side - Finish #1 |  |  |  | Portland Cement-Sand Plaster on Metal Lath
3/8 in.
Fire Side - Finish #2 |  |  |  | Gypsum-Sand Plaster on 3/8 in. gypsum lath | 0.58333
1/2 in.
Step 4: Detail Checks
Does thickness #1 non-fire side and fire side match? |  |  |  | Yes
Does thickness #2 non-fire side and fire side match? |  |  |  | Yes
Does the non-fire finish and fire side finish for finish #1 match? |  |  |  | Yes
Does the non-fire finish and fire side finish for finish #2 match? |  |  |  | Yes
Does the CMU contribute equal to or more than half of the total fire rating? |  |  |  | #REF!
|  | Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel |  | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag |  | 5.9 | 3.9994
Expanded clay, shale, or slate |  | 5.1 | 4.0322
Expanded slag or pumice |  | 4.7 | 4.0043
|  | Fire Rating of Finish Alone | 3.9986
Clear Data Entered on this Page

## Fire Resistance Rating
[6 empty] | Date: | 0
[6 empty] | Project Name: | 0
[6 empty] | Project Number: | 0
[6 empty] | Unit Description: | 0
Unit Composition
|  |  | Calcareous or Siliceous Gravel |  | 35%
|  |  | Limestone, Cinders or Unexpanded Slag | Limestone, Cinders or Unexpanded Slag | 25%
|  |  | Expanded clay, shale, or slate | Expanded clay, shale, or slate | 15%
|  |  | Expanded slag or pumice | Expanded slag or pumice | 25%
Fire Rating Based on Composition - Single Wythe CMU
| Equivalent Thickness of Unit |  |  | 8 | in.
|  | Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel |  | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag |  | 5.9 | 3.9994
Expanded clay, shale, or slate |  | 5.1 | 4.0322
Expanded slag or pumice |  | 4.7 | 4.0043
| Fire Rating of Unit |  |  | 3.9986 | hours
The following fire rating calculations were based off of ACI 216/1/TMS 216
[6 empty] | Date: | 0
[6 empty] | Project Name: | 0
[6 empty] | Project Number: | 0
[6 empty] | Unit Description: | 0
Unit Wythe Composition
|  |  | Calcareous or Siliceous Gravel |  | 35%
|  |  | Limestone, Cinders or Unexpanded Slag | Limestone, Cinders or Unexpanded Slag | 25%
|  |  | Expanded clay, shale, or slate | Expanded clay, shale, or slate | 15%
|  |  | Expanded slag or pumice | Expanded slag or pumice | 25%
Fire Rating Based on Multi-Wythe - Brick and CMU
| Fire Rating of Unit |  |  | 3.9986 | hours
| Equivalent Thickness for Clay Wythe #1 |  |  | 3 | in.
|  | Max/Min Equivalent Thickness Check - CMU #1 | Fire Rating - CMU #1 | Max/Min Equivalent Thickness Check - CMU #2 | Fire Rating - CMU #2
Calcareous or Siliceous Gravel |  | 3 | 1.1018 | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag |  | 3 | 1.1988 | 5.9 | 3.9994
Expanded clay, shale, or slate |  | 3 | 1.3556 | 5.1 | 4.0322
Expanded slag or pumice |  | 3 | 1.788 | 4.7 | 4.0043
|  | Wythe #1 - Max/Min Equiv. Thickness Check | Wythe #1 - Fire Rating | Wythe #2 - Max/Min Equiv. Thickness Check | Wythe #2 - Fire Rating
>=75% Solid |  | 3 | 1.2728 | 6 | 4.0001
Hollow |  | 3 | 1.5873 | 5 | 3.9889
Grouted |  | 3 | 0.9922 | 6.6 | 4.0124
| Fire Rating for Clay Wythe #1 |  |  | 1.2728 | hours
0
| Fire Rating of Assembly |  |  | 4 | hours
The following fire rating calculations were based off of ACI 216/1/TMS 216
[6 empty] | Date | 0 | #REF!
[6 empty] | Project Name: | 0 | #REF!
[6 empty] | Project Number: | 0 | #REF!
[6 empty] | Unit Description: | 0 | #REF!
Finishes
|  | Side #1 - Fire Side |  | Portland Cement-Sand Plaster on Metal Lath
3/8 in.
|  | Side #1 - Non-Fire Side |  | Portland Cement Sand Plaster
Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag
The following fire rating calculations were based off of ACI 216/1/TMS 216
Fire Rating Based on Finishes - Single Wythe CMU with Finish on one side
Non-Fire Side
|  | Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel |  | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag |  | 5.9 | 3.9994
Expanded clay, shale, or slate |  | 5.1 | 4.0322
Expanded slag or pumice |  | 4.7 | 4.0043
Fire Side
[6 empty] | Date | 0 | #REF!
[6 empty] | Project Name: | 0 | #REF!
[6 empty] | Project Number: | 0 | #REF!
[6 empty] | Unit Description: | 0 | #REF!
Finishes
|  | Side #1 - Fire Side |  | Portland Cement-Sand Plaster on Metal Lath
3/8 in.
|  | Side #1 - Non-Fire Side |  | Portland Cement Sand Plaster
Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag
|  | Side #2 - Fire Side |  | Gypsum-Sand Plaster on 3/8 in. gypsum lath
1/2 in.
|  | Side #2 - Non-Fire Side |  | Gypsum Sand Plaster
Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag
The following fire rating calculations were based off of ACI 216/1/TMS 216
Fire Rating Based on Finishes - Both Sides
Fire on Finish #1 Side
| Fire Side Finish #1 Fire Rating |  |  | 0 | hours
| Non-Fire Side Finish #2 Factor |  |  | 1.25
| Non-Fire Side Finish #2 Equivalent Thickness |  |  | 0.625 | in.
| Equivalent Thickness of Unit |  |  | 8 | in.
| Total Equivalent Thickness |  |  | 8.625 | in.
|  | Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel |  | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag |  | 5.9 | 3.9994
Expanded clay, shale, or slate |  | 5.1 | 4.0322
Expanded slag or pumice |  | 4.7 | 4.0043
| Total Non-Fire Side Fire Rating of Unit |  |  | 3.9986 | hours
| Total Fire Rating of Unit |  |  | 3.9986 | hours
Fire on Finish #2 Side
| Fire Side Finish #2 Fire Rating |  |  | 0.58333 | hours
| Non-Fire Side Finish #1 Factor |  |  | 1
| Non-Fire Side Finish #1 Equivalent Thickness |  |  | 0.5 | in.
| Equivalent Thickness of Unit |  |  | 8 | in.
| Total Equivalent Thickness |  |  | 8.5 | in.
|  | Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel |  | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag |  | 5.9 | 3.9994
Expanded clay, shale, or slate |  | 5.1 | 4.0322
Expanded slag or pumice |  | 4.7 | 4.0043
| Total Non-Fire Side Fire Rating of Unit |  |  | 3.9986 | hours
| Total Fire Rating of Unit |  |  | 4 | hours

## Fire Resistance Loop Tables (hidden)
Side 1
Non-Fire Side
| Finish | Aggregate Type
Type |  | Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag | 80% or more by volume of expanded shale_slate_clay_slag_pumice
Portland Cement Sand Plaster | 3/4 in. | 1 | 0.75
Portland Cement Sand Plaster | 7/8 in. | 1 | 0.75
Portland Cement Sand Plaster | 1 in. | 1 | 0.75
Gypsum Sand Plaster | 1/2 in. | 1.25 | 1
Gypsum Sand Plaster | 5/8 in. | 1.25 | 1
Gypsum Sand Plaster | 3/4 in. | 1.25 | 1
Gypsum Sand Plaster | 7/8 in. | 1.25 | 1
Gypsum Sand Plaster | 1 in. | 1.25 | 1
Gypsum Vermiculite or Perlite Plaster |  | 1.75 | 1.25
Gypsum Wallboard | 3/8 in. | 3 | 2.25
Gypsum Wallboard | 1/2 in. | 3 | 2.25
Gypsum Wallboard | 5/8 in. | 3 | 2.25
Gypsum Wallboard | Two Layers of 3/8 in. | 3 | 2.25
Gypsum Wallboard | One Layer of 3/8 in. and One layer of 1/2 in. | 3 | 2.25
Gypsum Wallboard | Two layers of 1/2 in. | 3 | 2.25
1
Fire Side
| Finish | Time (hr)
Gypsum Wallboard | 3/8 in. | 0.16667
Gypsum Wallboard | 1/2 in. | 0.25
Gypsum Wallboard | 5/8 in. | 0.33333
Gypsum Wallboard | Two Layers of 3/8 in. | 0.41667
Gypsum Wallboard | One Layer of 3/8 in. and One layer of 1/2 in. | 0.58333
Gypsum Wallboard | Two layers of 1/2 in. | 0.66667
Type 'X' Gypsum Wallboard | 1/2 in. | 0.41667
Type 'X' Gypsum Wallboard | 5/8 in. | 0.66667
Direct Applied Portland Cement | Direct Applied | 3.9986
Portland Cement-Sand Plaster on Metal Lath | 3/4 in. | 0.33333
Portland Cement-Sand Plaster on Metal Lath | 7/8 in. | 0.41667
Portland Cement-Sand Plaster on Metal Lath | 1 in. | 0.5
Gypsum-Sand Plaster on 3/8 in. gypsum lath | 1/2 in. | 0.58333
Gypsum-Sand Plaster on 3/8 in. gypsum lath | 5/8 in. | 0.66667
Gypsum-Sand Plaster on 3/8 in. gypsum lath | 3/4 in. | 0.83333
Gypsum-Sand Plaster on Metal Lath | 3/4 in. | 0.83333
Gypsum-Sand Plaster on Metal Lath | 7/8 in. | 1
Gypsum-Sand Plaster on Metal Lath | 1 in. | 1.3333
DIRECT APPLIED FIRE RATING CALCULATION
Fire Side Thickness | 0
Calcareous or Siliceous Gravel |  | 35
Limestone, Cinders or Unexpanded Slag |  | 25
Expanded clay, shale, or slate |  | 15
Expanded slag or pumice |  | 25
| Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag | 5.9 | 3.9994
Expanded clay, shale, or slate | 5.1 | 4.0322
Expanded slag or pumice | 4.7 | 4.0043
Side 2
Non-Fire Side
| Finish | Aggregate Type
Type |  | Siliceous_Calcareous_Limestone_Cinders_Air Cooled Blast Furnace Slag | 80% or more by volume of expanded shale_slate_clay_slag_pumice
Portland Cement Sand Plaster | 3/4 in. | 1 | 0.75
Portland Cement Sand Plaster | 7/8 in. | 1 | 0.75
Portland Cement Sand Plaster | 1 in. | 1 | 0.75
Gypsum Sand Plaster | 1/2 in. | 1.25 | 1
Gypsum Sand Plaster | 5/8 in. | 1.25 | 1
Gypsum Sand Plaster | 3/4 in. | 1.25 | 1
Gypsum Sand Plaster | 7/8 in. | 1.25 | 1
Gypsum Sand Plaster | 1 in. | 1.25 | 1
Gypsum Vermiculite or Perlite Plaster |  | 1.75 | 1.25
Gypsum Wallboard | 3/8 in. | 3 | 2.25
Gypsum Wallboard | 1/2 in. | 3 | 2.25
Gypsum Wallboard | 5/8 in. | 3 | 2.25
Gypsum Wallboard | Two Layers of 3/8 in. | 3 | 2.25
Gypsum Wallboard | One Layer of 3/8 in. and One layer of 1/2 in. | 3 | 2.25
Gypsum Wallboard | Two layers of 1/2 in. | 3 | 2.25
1.25
Fire Side
| Finish | Time (hr)
Gypsum Wallboard | 3/8 in. | 0.16667
Gypsum Wallboard | 1/2 in. | 0.25
Gypsum Wallboard | 5/8 in. | 0.33333
Gypsum Wallboard | Two Layers of 3/8 in. | 0.41667
Gypsum Wallboard | One Layer of 3/8 in. and One layer of 1/2 in. | 0.58333
Gypsum Wallboard | Two layers of 1/2 in. | 0.66667
Type 'X' Gypsum Wallboard | 1/2 in. | 0.41667
Type 'X' Gypsum Wallboard | 5/8 in. | 0.66667
Direct Applied Portland Cement | Direct Applied | 3.9986
Portland Cement-Sand Plaster on Metal Lath | 3/4 in. | 0.33333
Portland Cement-Sand Plaster on Metal Lath | 7/8 in. | 0.41667
Portland Cement-Sand Plaster on Metal Lath | 1 in. | 0.5
Gypsum-Sand Plaster on 3/8 in. gypsum lath | 1/2 in. | 0.58333
Gypsum-Sand Plaster on 3/8 in. gypsum lath | 5/8 in. | 0.66667
Gypsum-Sand Plaster on 3/8 in. gypsum lath | 3/4 in. | 0.83333
Gypsum-Sand Plaster on Metal Lath | 3/4 in. | 0.83333
Gypsum-Sand Plaster on Metal Lath | 7/8 in. | 1
Gypsum-Sand Plaster on Metal Lath | 1 in. | 1.3333
DIRECT APPLIED FIRE RATING CALCULATION
Direct Applied Thickness | 0
Calcareous or Siliceous Gravel |  | 35
Limestone, Cinders or Unexpanded Slag |  | 25
Expanded clay, shale, or slate |  | 15
Expanded slag or pumice |  | 25
| Max/Min Equivalent Thickness Check | Fire Rating
Calcareous or Siliceous Gravel | 6.2 | 3.9796
Limestone, Cinders or Unexpanded Slag | 5.9 | 3.9994
Expanded clay, shale, or slate | 5.1 | 4.0322
Expanded slag or pumice | 4.7 | 4.0043
Calculation for single wythe with finish on both sides - finish #1 side |  | #N/A
Calculation for single wythe with finish on both sides - finish #2 side |  | 0.58333

## Fire Resistance Lookup Graph (hidden)
Reference Table
| 4 | 3.75 | 3.5 | 3.25 | 3 | 2.75 | 2.5 | 2.25 | 2 | 1.75 | 1.5 | 1.25 | 1 | 0.75 | 0.5
Calcareous or Siliceous Gravel | 6.2 | 6 | 5.8 | 5.5 | 5.3 | 5 | 4.8 | 4.5 | 4.2 | 3.9 | 3.6 | 3.2 | 2.8 | 2.4 | 2
Limestone, Cinders or Unexpanded Slag | 5.9 | 5.7 | 5.5 | 5.2 | 5 | 4.8 | 4.5 | 4.3 | 4 | 3.7 | 3.4 | 3.1 | 2.7 | 2.3 | 1.9
Expanded clay, shale, or slate | 5.1 | 4.9 | 4.8 | 4.6 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.3 | 2.9 | 2.6 | 2.2 | 1.8
Expanded slag or pumice | 4.7 | 4.5 | 4.4 | 4.2 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3 | 2.7 | 2.5 | 2.1 | 1.9 | 1.5
| 4 | 3 | 2 | 1
>= 75% Solid | 6 | 4.9 | 3.8 | 2.7
Hollow | 5 | 4.3 | 3.4 | 2.3
Grouted | 6.6 | 5.5 | 4.4 | 3